## EFA PSBP Front Page
Distance to reach fully turbulent flow | 0 | m | set this to be zero if you want to allow entrainment to start as soon as air enters the room - this is the most optimistic assumption possible for a window
Width of opening window/damper | 4 | m
Average temperature of classroom | 21 | C
Height from floor to top of opening window/damper | 3 | m
Vertical height of opening high level window/damper | 0.5 | m
High level opening type | Top hung window
Number of occupants | 32
Minimum fresh air rate per person | 5 | l/s
This spreadsheet tool is based on standard plume theory from Turner (1973), Buoyancy Effects in Fluids. It also uses the concept of a virtual origin for plumes following the work of Kaye & Hunt. It shows how the temperature of an incoming stream of cold air through a high level window or damper into a warm room increases as the turbulent plume falls under gravity and entrains warm room air. The entrainment is just from one side of the line plume since the other side is against the window. When the temperature of the plume 1.4m from the floor (given by the blue line) is below the minimum acceptable level for schools (given by the red line), the system FAILS to meet the criterion for draughts as laid out in the June 2013 Facilities Output Specification. When the temperature of the plume (blue line) is above the minimum temperature (red line), the system PASSES the criterion for cold draughts.
The model assumes that the flow is fully turbulent the moment air enters the room. This is the most optimistic assumption with regards to the effectiveness of mixing. Note that the effects of gusts are also not accounted for. Finally, although entrainment is modelled only from one side of the plume, the reduced turbulence arising from the fact that the plume is constrained by a solid boundary is also not included. The modelling results therefore indicate an optimistic view of the mixing effectiveness and colder temperatures at the occupied level may be experienced.
The results should be interpreted as follows:
1) If the temperatures predicted show a FAIL then it is very likely that draughts will be a serious issue in your design and alternative solutions are recommended.
2) If the temperatures predicted show a MARGINAL PASS then anyone using this design should only do so with extreme caution as draughts may well still be a problem.
3) If the temperatures predicted show a CLEAR PASS then the designer can proceed, but note that the results do not guarantee draught free conditions at all times. If completely draught free conditions are desired under all weather conditions then alternative ventilation solutions should be pursued.
This spreadsheet tool was developed by Dr Shaun Fitzgerald, Breathing Buildings. It is free for designers to use to help them in the assessment of the most appropriate openings for wintertime ventilation. For more information please see www.breathingbuildings.com
Breathing Buildings is grateful to Prof Malcolm Cook (Loughborough University) and Prof Colm Caulfield (University of Cambridge) for discussions regarding the modelling of plumes.

## calcs
alpha T | 0.102
C | 0.11844
Vl source | 0.04 | cu m/s/m
Text | 15 | 14 | 13 | 12 | 11 | 10 | 9 | 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | -1 | -2 | -3
g prime source | 0.1962 | 0.2289 | 0.2616 | 0.2943 | 0.327 | 0.3597 | 0.3924 | 0.4251 | 0.4578 | 0.4905 | 0.5232 | 0.5559 | 0.5886 | 0.6213 | 0.654 | 0.6867 | 0.7194 | 0.7521 | 0.7848
Bo | 0.0094176 | 0.010987 | 0.012557 | 0.014126 | 0.015696 | 0.017266 | 0.018835 | 0.020405 | 0.021974 | 0.023544 | 0.025114 | 0.026683 | 0.028253 | 0.029822 | 0.031392 | 0.032962 | 0.034531 | 0.036101 | 0.03767
h virtual origin | 1.038 | 0.98605 | 0.94316 | 0.90689 | 0.87562 | 0.84827 | 0.82404 | 0.80237 | 0.78281 | 0.76503 | 0.74876 | 0.7338 | 0.71996 | 0.70712 | 0.69514 | 0.68394 | 0.67342 | 0.66353 | 0.65419
g prime floor | 0.095549 | 0.10853 | 0.12112 | 0.13338 | 0.14535 | 0.15706 | 0.16854 | 0.1798 | 0.19087 | 0.20176 | 0.21249 | 0.22305 | 0.23348 | 0.24377 | 0.25393 | 0.26397 | 0.2739 | 0.28373 | 0.29344
delT | 2.922 | 3.3189 | 3.704 | 4.079 | 4.4451 | 4.8032 | 5.1541 | 5.4986 | 5.8371 | 6.1701 | 6.498 | 6.8212 | 7.14 | 7.4547 | 7.7655 | 8.0726 | 8.3763 | 8.6766 | 8.9739
T head | 18.078 | 17.6811 | 17.296 | 16.921 | 16.5549 | 16.1968 | 15.8459 | 15.5014 | 15.1629 | 14.8299 | 14.502 | 14.1788 | 13.86 | 13.5453 | 13.2345 | 12.9274 | 12.6237 | 12.3234 | 12.0261
Min allowed C | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16
Height from entry point of cold air to critical point | 1.1 | m
Top hung window | 0
Bottom hung hopper window | 0.5
Damper | 0.125
Distance added | 0