## Inputs
CO2 Calculations
Data below calculated from 'State-of-the-Art Review of CO2 Demand Controlled Ventilation Technology and Application NISTIR 6729'
Occupant Age | Activity Level | Met Level | CO2 Generation (kg/s/p)
11 | Filing, seated | 1.2 | 6.1357e-06
Input Data | [10 empty] | Output
External CO2 Concentration | 390 | ppm | [8 empty] | average CO2 during occ day | 990.3454 | ppm
Fresh air ventilation rate per unit | 80 | l/s | [8 empty] | Assumed Total Ventilation Flow Rate | 160 | l/s
Number of units | 2
infiltration | 0.25 | ACH
Room Details
Room Area | 60 | m2
Room Height | 3 | m
Calculation for contaminant build up
|  | Occupancy |  | v (cu m/s) | V (cu m) | c (kg/kg) | x (CO2 added in kg/s) | A | Q | CO2 (ppm) | time | CO2 (ppm) | occupancy | average CO2 (ppm) during occ day
| 8:00 | 0 |  | 0.1725 | 180 | 0.00039 | 0 | 0 | 0.00039 | 390 | 8:00 | 390 | 0 | 990.3454
| 8:15 | 0 |  | 0.1725 | 180 | 0.00039 | 0 | 0 | 0.00039 | 390 | 8:15 | 390 | 0 | 990.3454
| 8:30 | 0 |  | 0.1725 | 180 | 0.00039 | 0 | 0 | 0.00039 | 390 | 8:30 | 390 | 0 | 990.3454
| 8:45 | 0 |  | 0.1725 | 180 | 0.00039 | 0 | 0 | 0.00039 | 390 | 8:45 | 390 | 0 | 990.3454
| 9:00 | 32 |  | 0.1725 | 180 | 0.00039 | 0.00019634 | -0.00094852 | 0.0013385 | 390 | 9:00 | 390 | 32 | 990.3454
| 9:15 | 2 |  | 0.1725 | 180 | 0.00093814 | 1.2271e-05 | 0.00048886 | 0.00044928 | 938.1421 | 9:15 | 938.1421 | 2 | 990.3454
| 9:30 | 32 |  | 0.1725 | 180 | 0.00065563 | 0.00019634 | -0.00068288 | 0.0013385 | 655.6327 | 9:30 | 655.6327 | 32 | 990.3454
| 9:45 | 32 |  | 0.1725 | 180 | 0.0010503 | 0.00019634 | -0.00028825 | 0.0013385 | 1050.2671 | 9:45 | 1050.2671 | 32 | 990.3454
| 10:00 | 32 |  | 0.1725 | 180 | 0.0012168 | 0.00019634 | -0.00012167 | 0.0013385 | 1216.8445 | 10:00 | 1216.8445 | 32 | 990.3454
| 10:15 | 32 |  | 0.1725 | 180 | 0.0012872 | 0.00019634 | -5.1358e-05 | 0.0013385 | 1287.1577 | 10:15 | 1287.1577 | 32 | 990.3454
| 10:30 | 2 |  | 0.1725 | 180 | 0.0013168 | 1.2271e-05 | 0.00086756 | 0.00044928 | 1316.8373 | 10:30 | 1316.8373 | 2 | 990.3454
| 10:45 | 2 |  | 0.1725 | 180 | 0.00081548 | 1.2271e-05 | 0.0003662 | 0.00044928 | 815.482 | 10:45 | 815.482 | 2 | 990.3454
| 11:00 | 32 |  | 0.1725 | 180 | 0.00060386 | 0.00019634 | -0.00073466 | 0.0013385 | 603.8572 | 11:00 | 603.8572 | 32 | 990.3454
| 11:15 | 32 |  | 0.1725 | 180 | 0.0010284 | 0.00019634 | -0.0003101 | 0.0013385 | 1028.4124 | 11:15 | 1028.4124 | 32 | 990.3454
| 11:30 | 32 |  | 0.1725 | 180 | 0.0012076 | 0.00019634 | -0.0001309 | 0.0013385 | 1207.6195 | 11:30 | 1207.6195 | 32 | 990.3454
| 11:45 | 32 |  | 0.1725 | 180 | 0.0012833 | 0.00019634 | -5.5252e-05 | 0.0013385 | 1283.2638 | 11:45 | 1283.2638 | 32 | 990.3454
| 12:00 | 2 |  | 0.1725 | 180 | 0.0013152 | 1.2271e-05 | 0.00086591 | 0.00044928 | 1315.1937 | 12:00 | 1315.1937 | 2 | 990.3454
| 12:15 | 2 |  | 0.1725 | 180 | 0.00081479 | 1.2271e-05 | 0.00036551 | 0.00044928 | 814.7882 | 12:15 | 814.7882 | 2 | 990.3454
| 12:30 | 2 |  | 0.1725 | 180 | 0.00060356 | 1.2271e-05 | 0.00015428 | 0.00044928 | 603.5643 | 12:30 | 603.5643 | 2 | 990.3454
| 12:45 | 2 |  | 0.1725 | 180 | 0.00051441 | 1.2271e-05 | 6.5123e-05 | 0.00044928 | 514.4056 | 12:45 | 514.4056 | 2 | 990.3454
| 13:00 | 32 |  | 0.1725 | 180 | 0.00047677 | 0.00019634 | -0.00086174 | 0.0013385 | 476.7712 | 13:00 | 476.7712 | 32 | 990.3454
| 13:15 | 32 |  | 0.1725 | 180 | 0.00097477 | 0.00019634 | -0.00036375 | 0.0013385 | 974.7687 | 13:15 | 974.7687 | 32 | 990.3454
| 13:30 | 32 |  | 0.1725 | 180 | 0.001185 | 0.00019634 | -0.00015354 | 0.0013385 | 1184.9762 | 13:30 | 1184.9762 | 32 | 990.3454
| 13:45 | 32 |  | 0.1725 | 180 | 0.0012737 | 0.00019634 | -6.481e-05 | 0.0013385 | 1273.7059 | 13:45 | 1273.7059 | 32 | 990.3454
| 14:00 | 2 |  | 0.1725 | 180 | 0.0013112 | 1.2271e-05 | 0.00086188 | 0.00044928 | 1311.1592 | 14:00 | 1311.1592 | 2 | 990.3454
| 14:15 | 32 |  | 0.1725 | 180 | 0.00081309 | 0.00019634 | -0.00052543 | 0.0013385 | 813.0853 | 14:15 | 813.0853 | 32 | 990.3454
| 14:30 | 32 |  | 0.1725 | 180 | 0.0011167 | 0.00019634 | -0.00022179 | 0.0013385 | 1116.7287 | 14:30 | 1116.7287 | 32 | 990.3454
| 14:45 | 32 |  | 0.1725 | 180 | 0.0012449 | 0.00019634 | -9.3618e-05 | 0.0013385 | 1244.8983 | 14:45 | 1244.8983 | 32 | 990.3454
| 15:00 | 32 |  | 0.1725 | 180 | 0.001299 | 0.00019634 | -3.9516e-05 | 0.0013385 | 1298.9994 | 15:00 | 1298.9994 | 32 | 990.3454
| 15:15 | 8 |  | 0.1725 | 180 | 0.0013218 | 4.9086e-05 | 0.00069471 | 0.00062713 | 1321.8358 | 15:15 | 1321.8358 | 8 | 990.3454
| 15:30 | 8 |  | 0.1725 | 180 | 0.00092037 | 4.9086e-05 | 0.00029324 | 0.00062713 | 920.3685 | 15:30 | 920.3685 | 8 | 990.3454
| 15:45 | 8 |  | 0.1725 | 180 | 0.00075091 | 4.9086e-05 | 0.00012378 | 0.00062713 | 750.907 | 15:45 | 750.907 | 8 | 990.3454
| 16:00 | 0 |  | 0.1725 | 180 | 0.00067938 | 0 | 0.00028938 | 0.00039 | 679.3764 | 16:00 | 679.3764 | 0 | 990.3454
| 16:15 | 0 |  | 0.1725 | 180 | 0.00051215 | 0 | 0.00012215 | 0.00039 | 512.1474 | 16:15 | 512.1474 | 0 | 990.3454
| 16:30 | 0 |  | 0.1725 | 180 | 0.00044156 | 0 | 5.1559e-05 | 0.00039 | 441.5591 | 16:30 | 441.5591 | 0 | 990.3454
| 16:45 | 0 |  | 0.1725 | 180 | 0.00041176 | 0 | 2.1763e-05 | 0.00039 | 411.7634 | 16:45 | 411.7634 | 0 | 990.3454
| 17:00 | 0 |  | 0.1725 | 180 | 0.00039919 | 0 | 9.1864e-06 | 0.00039 | 399.1864 | 17:00 | 399.1864 | 0 | 990.3454
| 17:15 | 0 |  | 0.1725 | 180 | 0.00039388 | 0 | 3.8776e-06 | 0.00039 | 393.8776 | 17:15 | 393.8776 | 0 | 990.3454
| 17:30 | 0 |  | 0.1725 | 180 | 0.00039164 | 0 | 1.6368e-06 | 0.00039 | 391.6368 | 17:30 | 391.6368 | 0 | 990.3454
| 17:45 | 0 |  | 0.1725 | 180 | 0.00039069 | 0 | 6.9089e-07 | 0.00039 | 390.6909 | 17:45 | 390.6909 | 0 | 990.3454
| 18:00 | 0 |  | 0.1725 | 180 | 0.00039029 | 0 | 2.9163e-07 | 0.00039 | 390.2916 | 18:00 | 390.2916 | 0 | 990.3454
| 18:15 | 0 |  | 0.1725 | 180 | 0.00039012 | 0 | 1.231e-07 | 0.00039 | 390.1231 | 18:15 | 390.1231 | 0 | 990.3454
| 18:30 | 0 |  | 0.1725 | 180 | 0.00039005 | 0 | 5.196e-08 | 0.00039 | 390.052 | 18:30 | 390.052 | 0 | 990.3454
| 18:45 | 0 |  | 0.1725 | 180 | 0.00039002 | 0 | 2.1933e-08 | 0.00039 | 390.0219 | 18:45 | 390.0219 | 0 | 990.3454
| 19:00 | 0 |  | 0.1725 | 180 | 0.00039001 | 0 | 9.258e-09 | 0.00039 | 390.0093 | 19:00 | 390.0093 | 0 | 990.3454
| 19:15 | 0 |  | 0.1725 | 180 | 0.00039 | 0 | 3.9078e-09 | 0.00039 | 390.0039 | 19:15 | 390.0039 | 0 | 990.3454
| 19:30 | 0 |  | 0.1725 | 180 | 0.00039 | 0 | 1.6495e-09 | 0.00039 | 390.0016 | 19:30 | 390.0016 | 0 | 990.3454
| 19:45 | 0 |  | 0.1725 | 180 | 0.00039 | 0 | 6.9627e-10 | 0.00039 | 390.0007 | 19:45 | 390.0007 | 0 | 990.3454
| 20:00 | 0 |  | 0.1725 | 180 | 0.00039 | 0 | 2.939e-10 | 0.00039 | 390.0003 | 20:00 | 390.0003 | 0 | 990.3454
| 20:15 | 0 |  | 0.1725 | 180 | 0.00039 | 0 | 1.2406e-10 | 0.00039 | 390.0001 | 20:15 | 390.0001 | 0 | 990.3454
| 20:30 | 0 |  | 0.1725 | 180 | 0.00039 | 0 | 5.2365e-11 | 0.00039 | 390.0001 | 20:30 | 390.0001 | 0 | 990.3454
| 20:45 | 0 |  | 0.1725 | 180 | 0.00039 | 0 | 2.2104e-11 | 0.00039 | 390 | 20:45 | 390 | 0 | 990.3454
| 21:00 | 0 |  | 0.1725 | 180 | 0.00039 | 0 | 9.33e-12 | 0.00039 | 390 | 21:00 | 390 | 0 | 990.3454
This tool solves the first order differential equation for build up of CO2 in a room ventilated at a specific rate. The daily average CO2 is taken to be during the period when the room is occupied. If the room has an occupancy of zero it is considered unoccupied and is therefore excluded from the average.
Note on C24: This column needs to be manually updated.

## Data (hidden)
50 Percentile Data from Royal College of Paediatrics and Child Health
UK Growth Chart 2-18 years, Boys
Age (yrs) | Height (m) | Weight (kg) | AD (m2) | Activity | Met | Respiratory Quotient, RQ | CO2 density (kg/m3)
3 | 0.96 | 14 | 0.60499 | Reading, seated | 1 | 0.83 | 1.799
7 | 1.22 | 23 | 0.88888 | Typing | 1.1
11 | 1.43 | 35 | 1.1922 | Filing, seated | 1.2
16 | 1.73 | 61 | 1.7332 | Filing, standing | 1.4
Adult | 1.77 | 67 | 1.8338 | Walking (2mph) | 2
|  |  |  | Housework | 3
|  |  |  | Exercise | 4